# Borehole Water Supply Verification Checklist

Residential Building (Basement, G+1) | Kribi, Cameroon
Standards Reference: MINEE Regulations, ANOR/ISO 24510, WHO Guidelines, IEC

# 1. Siting, Legal & Hydrogeological Verification (MINEE & Local Codes)

[   ]  Permits & Declarations: Has the borehole been declared/authorized by the Ministry of Water and Energy (MINEE) as per local groundwater regulations?

[   ]  Safe Siting Distances: Is the borehole located at least 35 meters away from septic tanks or sanitation systems to prevent contamination?

[   ]  Flood Protection: Is the borehole positioned on elevated ground (non-flooding location), critical for Kribi's heavy rainfall and coastal context?

[   ]  Hydrogeological Report: Is there a formal siting report (geophysical survey) justifying the selected drilling point?

# 2. Drilling, Casing & Filtration (ISO / DIN Standards)

[   ]  Casing Material: Are the PVC or steel casings certified to international standards (e.g., DIN or IS 12818) and suitable for potable water?

[   ]  Diameter Compliance: Is the nominal diameter of the casing adequate (minimum 100mm to 125mm) to accommodate the submersible pump?

[   ]  Gravel Pack & Screen: Is the gravel pack (massif filtrant) properly sized and washed, and is the screen correctly placed at the aquifer level to prevent sand ingress?

[   ]  Sanitary Seal (Grouting): Is the annular space near the surface properly grouted with bentonite/cement to prevent surface water runoff from entering the aquifer?

# 3. Pumping Test & Water Quality (WHO Guidelines / ANOR)

[   ]  Yield & Step-Drawdown Test: Has a continuous pumping test (minimum 24-48 hours) been conducted to determine the exact yield, dynamic water level, and aquifer recovery rate?

[   ]  Water Quality Sampling: Were water samples taken at the end of the pumping test for physical, chemical, and bacteriological analysis by a certified laboratory?

[   ]  WHO / Local Compliance: Do the laboratory results meet the WHO Guidelines for Drinking-water Quality and Cameroon's ANOR standards for heavy metals (iron/manganese, common in Kribi) and E. coli?

[   ]  Disinfection: Has the borehole been properly shock-chlorinated (disinfected) after drilling and pump installation?

# 4. Equipment, Storage & Commissioning (IEC 60364)

[   ]  Submersible Pump Electricals: Are the pump motor, cables, and control panels verified against IEC electrical safety standards, including proper earthing and surge protection?

[   ]  Dry-Run Protection: Is the control panel equipped with water-level sensors (electrodes) to automatically shut off the pump if the water level drops too low?

[   ]  Storage & Treatment: If water quality requires it, are filtration systems (e.g., UV, reverse osmosis, iron removal) and a food-grade overhead storage tank verified and commissioned?

[   ]  Wellhead Capping: Is a secure, locked, and approved sanitary cap installed over the wellhead to prevent unauthorized access and contamination?