# Electrical Verification & Engineer Responsibilities Report

Project: Residential Building (Basement, G+1)
Location: Kribi, South Region, Cameroon
Standards Reference: NF C 15-100, IEC 60364 (Low-Voltage Electrical Installations)

--------------------------------------------------------------------------------

# 1. Electrical Engineer Responsibilities & Liabilities

The verifying Electrical Engineer is legally and technically responsible for certifying that the electrical installation poses no fire hazard, protects occupants from electric shock (especially in Kribi’s high-humidity/wet coastal environment), and can safely carry the designed load. Specifically, the engineer must:

Verify that all materials (cables, breakers, panels) are original, uncompromised, and meet IEC/NF C standard ratings.

Witness and sign off on all hidden works (conduit routing in slabs/walls) BEFORE they are permanently covered by concrete or plaster.

Conduct physical instrumentation testing (Insulation Resistance, Earth Loop Impedance) rather than relying solely on visual inspections.

Ensure stringent safety protocols for the basement level, including water-resistant (IP-rated) fittings and isolated sump pump circuits.

## 2. Phase 1: First Fix (Wiring & Conduiting - Pre-Covering)

| Verification Element | Required Standard / Specification | Verification Method | Status |
| --- | --- | --- | --- |
| Conduit Routing & Depth | Conduits must not cluster excessively (weakening concrete). Wall chases must be strictly vertical/horizontal. | Visual inspection before pouring concrete or plastering. | [ ] Pass [ ] Fail |
| Wire Sizing (Cross-Section) | Minimum 1.5mm² for lighting; 2.5mm² for standard sockets; 4.0mm² to 6.0mm² for ACs/Ovens. | Strip wire jacket and verify copper thickness using wire gauge or digital caliper. | [ ] Pass [ ] Fail |
| Color Coding Convention | Strict adherence: Phase (Red/Brown), Neutral (Blue), Earth (Green/Yellow). | Visual check at all junction boxes and terminations. | [ ] Pass [ ] Fail |
| Basement Wiring | All basement junction boxes must be IP65 rated (waterproof) due to flood risks. | Visual verification of IP ratings on box covers and cable glands. | [ ] Pass [ ] Fail |

## 3. Phase 2: Distribution Boards & Protection Devices

| Verification Element | Required Standard / Specification | Verification Method | Status |
| --- | --- | --- | --- |
| Main Breaker Sizing | Main incoming breaker must match the calculated total load and ENEO grid supply rating. | Compare SLD (Single Line Diagram) calculations against installed physical breaker. | [ ] Pass [ ] Fail |
| RCD / RCBO Protection | 30mA Residual Current Devices MUST be installed for all bathroom, kitchen, and basement circuits. | Physical test button check on breaker and cross-reference with circuit map. | [ ] Pass [ ] Fail |
| Panel Location | Distribution boards must be easily accessible, at eye level (1.5m - 1.8m), and strictly outside wet zones. | Tape measure height; verify distance from water sources. | [ ] Pass [ ] Fail |
| Phase Balancing | Three-phase systems must have loads evenly distributed to prevent neutral wire overload. | Clamp meter readings on each phase under simulated full load. | [ ] Pass [ ] Fail |

## 4. Phase 3: Final Instrumentation Testing & Commissioning

| Verification Element | Required Standard / Specification | Verification Method | Status |
| --- | --- | --- | --- |
| Earthing (Grounding) Resistance | Earth pit resistance must be < 10 ohms (NF C 15-100 standard). | Digital Earth Resistance Tester (3-pole method) at the grounding rod. | [ ] Pass [ ] Fail |
| Insulation Resistance (Megger) | Resistance between Phase-Neutral and Phase-Earth must be > 1.0 Megohm at 500V DC. | Megohmmeter applied to isolated circuits before connecting appliances. | [ ] Pass [ ] Fail |
| Continuity Testing | Unbroken path for all Earth (Green/Yellow) wires from the main panel to the furthest socket. | Multimeter continuity (beep) test. | [ ] Pass [ ] Fail |
| Polarity Check | Live (Phase) must be connected to the right pin of the socket; Neutral to the left; Earth to the top. | Socket tester plug applied to every receptacle in the building. | [ ] Pass [ ] Fail |

# 5. Verifying Electrical Engineer Sign-Off

By signing below, I certify that I have physically executed or witnessed the above tests. The electrical installation complies with NF C 15-100/IEC 60364 standards and is safe for ENEO grid connection and permanent habitation.

Name of Verifying Engineer: _______________________________________

Professional License Number: ______________________________________

Date of Verification: ______________________________________________

Signature & Stamp: ___________________________