# Plumbing Sub-Stages & Water Pressure Verification Report

Project: Residential Building (Basement, G+1)
Location: Kribi, South Region, Cameroon
Standards Reference: NF DTU 60.1 / 60.11, International Plumbing Code (IPC)

--------------------------------------------------------------------------------

# 1. Context & Pressure Flow Mandates

Municipal water supply (CAMWATER) in Kribi can fluctuate. A G+1 residential building requires a verified overhead tank and booster pump system to maintain adequate flow to the first-floor showers, while the basement requires strict backflow prevention against the high coastal water table. This report divides verification into three strict sub-stages: Rough-in, Pressure/Hydrostatic Testing, and Final Flow Commissioning.

## 2. Sub-Stage 1: Rough-in (First Fix) Verification

| Verification Element | Required Standard / Specification | Verification Method | Status |
| --- | --- | --- | --- |
| Pipe Material & Sizing | PPR for hot/cold supply (PN20 rating). PVC for drainage (SN4/SN8 for buried). | Check manufacturer markings on pipes prior to installation. | [ ] Pass [ ] Fail |
| Drainage Slope (Gradient) | Minimum 1.5% to 2.0% slope for all horizontal soil and waste pipes. | Use a digital spirit level or laser level along pipe runs before covering. | [ ] Pass [ ] Fail |
| Pipe Chasing & Sleeves | No structural rebar cut during wall chasing. Pipes passing through beams/slabs must use PVC sleeves. | Visual inspection before plastering or concrete pouring. | [ ] Pass [ ] Fail |
| Ventilation Stacks | Soil/waste pipes must vent through the roof to prevent vacuum siphoning of P-traps. | Trace vent lines to the roof exit point. | [ ] Pass [ ] Fail |

## 3. Sub-Stage 2: Hydrostatic & Leak Testing (Pre-Covering)

| Verification Element | Required Standard / Specification | Verification Method | Status |
| --- | --- | --- | --- |
| Hydrostatic Pressure Test (Supply) | Test at 1.5x the working pressure (typically 10 Bar / 150 PSI) for a minimum of 2 hours with ZERO pressure drop. | Seal all outlets, connect a manual hydraulic pressure test pump with a calibrated gauge, and monitor for pressure loss. | [ ] Pass [ ] Fail |
| Drainage Water Test (Static) | Fill drainage system with water to a height of 3 meters above the highest joint for 15 minutes. No leaks allowed. | Plug lower drainage exits, fill from top, and visually inspect every joint for weeping. | [ ] Pass [ ] Fail |
| Thermal Expansion Limits | Hot water PPR pipes must have expansion loops or adequate clipping to prevent buckling under pressure and heat. | Tape measure distance between pipe clips (max 1.2m for 20mm pipe). | [ ] Pass [ ] Fail |

## 4. Sub-Stage 3: Final Flow Pressure & Commissioning

| Verification Element | Required Standard / Specification | Verification Method | Status |
| --- | --- | --- | --- |
| Dynamic Water Pressure (Showers/Taps) | Minimum dynamic pressure of 1.5 Bar (20 PSI) and max 4.0 Bar (60 PSI) at the highest first-floor fixture. | Attach a water pressure gauge to the furthest/highest showerhead or tap while water is flowing. | [ ] Pass [ ] Fail |
| Booster Pump Cut-in/Cut-out | Pump must activate smoothly when pressure drops and shut off without water hammer (banging pipes). | Run multiple taps simultaneously; observe pump pressure switch calibration. | [ ] Pass [ ] Fail |
| Basement Backflow & Sump Pump | Non-return (backwater) valves installed on basement drains. Sump pump triggers automatically via float switch. | Manually fill sump pit to trigger pump; verify non-return valve orientation. | [ ] Pass [ ] Fail |
| Water Heater Relief Valve | Temperature & Pressure (T&P) relief valve must be installed and pipe routed safely to a drain. | Visual check; manual trip of the T&P lever to verify discharge. | [ ] Pass [ ] Fail |

# 5. Verifying Plumbing Engineer Sign-Off

By signing below, I certify that the plumbing installation has been hydrostatically tested, demonstrates adequate dynamic flow pressure across all floors, and includes necessary basement flood protections in accordance with local and international codes.

Name of Verifying Engineer: _______________________________________

Professional License Number: ______________________________________

Date of Verification: ______________________________________________

Signature & Stamp: ___________________________